THIS IS NOT A CONSTRUCTION DOCUMENT - Edit with care to suit project requirements.  User must determine final content suitability in whole or part for the specific project. 


SPI – Specialty Products

 & Insulation 
C/O Dunes Point Capital

  411 Theodore Fremd Ave.  
Rye, NY 10580
Phone (855) 519-4044 

E-mail: fabteam@spi-co.com

www.spi-co.com
SECTIONS

07 84 13 Penetration Fire Stopping

07 21 00 Thermal Insulation 

09 81 13 Acoustic Board Insulation

07 21 13.19 Mineral Board Insulation 
PART 1 GENERAL 
1.01 SUMMARY 

A. An enclosure for recessed ceiling fixture fire protection, sound blocking and thermal insulation.
Specifier Note: Revise paragraphs below to suit project requirements. 

1.02 REFERENCES

A. ASTM International:

1. ASTM E84, Standard Test Method for Surface Burning Characteristics of Building Materials
2. ASTM E136, Standard Test Method for Behavior of Materials in a Vertical Tube Furnace at 750°C

3. ASTM C518, Standard Test Method for Steady-State Thermal Transmission Properties by Means of the Heat Flow Meter Apparatus

4. ASTM E119, Standard Test Methods for Fire Tests of Building Construction and Materials
5. ASTM E1414, Standard Test Method for Airborne Sound Attenuation Between Rooms Sharing a Common Ceiling Plenum

6. ASTM C1104, Standard Test Method for Determining the Water Vapor Sorption of Unfaced Mineral Fiber Insulation
B. National Fire Protection Association (NFPA)
1. NFPA 220, Standard on Types of Building Construction 
C. UL / ULC Approvals: 
a. UL 263, Fire Tests of Building Construction and Materials
b. UL 723,  Surface Burning Characteristics of Building Materials
c. Luminaires, Luminaire Assemblies and Luminaire Enclosures Classified For Fire Resistance (CDHW and IFDL)

d. UL Design listings: 

1. Floor-Ceiling Design: D010, D216, D219, G230, G234, G258, G523, G526, J202, L006

2. Roof-Ceiling Design: P207, P228, P230, P237, P267

e. UL Canada (ULC) Approvals: 
1. CAN/ULC-S101, Fire Endurance Tests of Building Construction and Materials
2. Luminaires, Luminaire Assemblies and Luminaire Enclosures Classified for Fire Resistance (CDHW7 and IFDL7)

D. International Building Code (IBC): 2006, 2009, 2012 Editions 
1.1 Work in this section is subject to drawings, general conditions, schedules, addenda and other contract documents.

1.2 The extent of ceiling fixture covers to be installed is shown on project drawings and schedules.

1.3 Submit manufacturer current product technical literature and installation instructions. 

1.4 Samples: provide a sample enclosure. 
1.5 UL listed covers shall be installed according to manufacture’s recommendations and instructions.

1.6 Installation shall not begin until all wet work (plastering, concrete, etc.) is completed and dry.  Building shall be properly enclosed before installation. 
1.7 The contractor shall be responsible for the examination and acceptance of covers and conditions prior to cover installation.

1.8 Substitutions: Not permitted. 

PART 2 MATERIALS
2.1 Fire Protection, Acoustical and Thermal Ceiling Fixture Enclosure as manufactured by 
SPI – Specialty Products & Insulation, C/O Dunes Point Capital, 411 Theodore Fremd Ave.,  Rye, NY  10580.  Phone (855) 519-4044, email: fabteam@spi-co.com  web: www.spi-co.com.

2.2 Basis of Design SafeLite®   Patent / U.S. Patent Registration No. 7,627, 999 B2
2.3 Fixture enclosures shall be constructed as per manufacturer technical information and installation instructions. 
A. Fixture enclosures to be supplied by one manufacturer for all fluorescent lights, can lights and speaker high hats listed on drawings and schedules.
B. IC rated and Non IC rated fixture enclosures are to be factory sized for proper fixture fit and to meet fixture clearance requirements.  
2.4 Fixture enclosure material to be classified per ASTM E84 as Class A fire rated, Flame Spread 25 maximum, Smoke Development 0 maximum.
2.5 Fixture enclosure material to be classified as non-combustible in accordance with ASTM E136 (NFPA Standard 220).
2.6 Fixture enclosure material to contain 70 - 90% recycled content and contribute to LEED credit. 

2.7 Fixture enclosure material to have an R value of 4.2 per inch @ 75 ° F per ASTM C 518.
2.8 Fixture enclosure to have documented Ceiling Attenuation Class (CAC) performance in accordance with ASTM E-1414. 

2.9 Fixture enclosure to have documented acoustical noise reduction coefficient (NRC) in accordance with ASTM C-423, providing an NRC value of 1.00 at 1 inch thick. 

PART 3 EXECUTION


3.1 Examination
A. Provide accurate field measurements for specific fixture model / style number as required to achieve proper fit of fabricated fixture enclosure.  
B. Measurements to be provided in a timely manner to prevent impact to project construction schedule.

3.2 Cover Installation

A. Installation shall be in accordance with manufacturer’s installation instructions and diagrams. 

3.3 Delivery, Storage and Handling
A. Deliver enclosure materials and components in manufacturer original, unopened, undamaged packaging with identification labels intact. 
B. Store enclosure materials and components in a clean, dry, protected area. 
C. Do not stack skid materials. 

END OF SECTION













11.18
